Design, drilling and testing of HBKW4 at Kilinto Brewery, Addis Ababa, Ethiopia

Completion report

| Colofon |  |  |
| --- | --- | --- |
| Document title | . | Design, drilling and testing of HBKW4 at Kilinto Brewery, Addis Ababa, Ethiopia |
| Client | . | HBSC |
| Status | . | Completion report |
| Date | . | 29 juni 2016 |
| Project number | . | 685 |
| Project team | . | Theo Kleinendorst, Mesfin Aytenfisu |
| Disclaimer |  |  |
| CONCEPT Working document: This document has the status of concept working document. No rights can be derived. The authors are not responsible for possible errors or consequences. |  |  |

Contents

1	Introduction	4

2	Well construction	6

2.1	Drilling	6

2.2	Geophysical logging	6

2.3	Casing installation	7

2.4	Development	7

3	Pumping tests	9

3.1	Step test	9

3.2	Aquifer test	10

3.3	Recovery test	11

4	Water quality	13

5	Recommended operation	14

#### Tables

Table 1 Salient features HBKW4	5

Table 2 Casing arrangement HBKW4	7

Table 3 Step drawdown test	9

#### Figures

Figure 1 Well locations Kalinto Brewery	4

Figure 2 Washed basalt gravel	7

Figure 3 Development by airlifting	8

Figure 4 Discharge - drawdown graph of step test	9

Figure 5 Time - drawdown graph of aquifer test (30 lps)	10

Figure 6 Drawdown in HBKW3 during aquifer test on HBKW4	11

Figure 7 Recovery test on HBKW4	12

Figure 8 Theis’ recovery graph for HBKW4	12

Figure 9 Development of dynamic water level in HBKW4 due to pumping at 90, 110 and 130 m3/h	14

# Introduction

For the water supply of the second phase of the Kalinto Brewery at Addis Ababa, Ethiopia, HBSC has contracted ECC Energy PLC to drill two wells to a depth of 500 meter. Acacia Water and MS Consultancy were responsible for the supervision of the works. The wells (HBKW3 and HBKW4) were constructed in the period between February and May 2016.

This is the completion report of well HBKW4. The completion report of well HBKW3 is published in a separate document.

Figure 1 Well locations Kalinto Brewery

Well HBKW4 is located on the south-eastern corner of the premises of the brewery (see figure 1). Salient features of HBKW4 are presented below.

Table 1 Salient features HBKW4

| Location | Addis Ababa, Kaliti, Kilinto Area |
| --- | --- |
| Coordinates | 479157E, 983456N (Adindan, UTM 37 N) |
| Elevation | 2187.5 m |
| Drilling Contractor | ECC Energy PLC |
| Drilling rig | ZJ-350HP RIG,15001 |
| Drilling Method | Mud Rotary |
| Drilling Commenced | March 8, 2016 |
| Drilling Completed | April 10, 2016 |
| Total Drilled Depth | 505 m |
| Total Cased Section | 502 m |
| Drilling diameters | diameter (inch); Top (m); Bottom (m). 26; 0; 12. 17; 12; 154. 12; 154; 505. |
| Casing Installation | Item; Material; Diameter (in); Length (m). Bottom pipe; SS 304; 6 5/8; 1. Screen; SS 304; 6 5/8; 68.5. Casing pipe; SS 304; 6 5/8; 283. Dielectric joint; Dual; 6 5/8 to 12; 1. Casing pipe; API; 12; 145. Screen; API; 12; 5.8. |
| Static water level | 47.38 m bgl |
| Pumping test | Discharge; 30 lps (108 m3/h). Duration; 7200 min (5 days). Drawdown; 54.9 m. EC; 659 µS/cm. Temperature; 35.1 °C. |
| Local transmissivity | 64 m2/d |
| Regional transmissivity | 152 m2/d |
| Storativity | 5.12e-4 |
| Design capacity | 110 m3/h |
| Dynamic water level | 117 m bgl |
| Effective yearly production | 825,000 m3 |
| Pump setting | 138 m |
| Well efficiency | 92% |

# Well construction

## Drilling

The area around the brewery is composed of basic volcanic and acidic rocks and pyroclastic units. The major rocky units include basalt, ignimbrite, welded tuff, scoraceous basalt and scoria at different scales of weathering and ages. In most cases, the massive rocky units with high fracture and tectonic effects are the major aquifer units. The contact zone between successive layers is one best aquifer zone for the wells drilled around.

Drilling operation was carried out between 8 March 2016 and 10 April 2016. The drilling machine was ZJ-350HP RIG single drum CAT C9 engine 900KN, pulling capacity with 400HP draw work, N3NB-1300 mud pump and 12VB diesel engine, designated as 15001.

The drilling method applied is direct mud rotary. Bentonite clay, foam, air and water were used during the drilling. Cuttings were collected and logged every two meters interval.

The first 12 meter was dilled by 26’’ rock bit and a 22’’ diameter surface /sanitary casing is installed down to 12m depth. The diameter of the well is telescopic: 17‘’ diameter (12 to 154 m), and 12 inch diameter from 154 m to 505m.

The cuttings consist of pyroclastic materials, ignimbrites and tuff and volcanic sand, scoraceous basalt and weathered and fresh basalt. Samples were taken every two meters and stored in steel sample boxes.

Electrical conductivity, temperature, drilling rate, mud properties (sand content, viscosity, density etc.) checked on periodic intervals with the progress in drilling depth.

## Geophysical logging

The open borehole was logged on 10 April for resistivity and natural gamma radiation. The Long Normal, Short Normal, Spontaneous Potential and Natural Gamma logs are presented on the borehole logs in Annex 1.

The combination of low gamma and low resistivity is believed to reflect fractured zones with low clay content that may be water bearing. These zones were targeted for the screen setting.

## Casing installation

The upper 143 m is cased with 12 inch nominal diameter (ND) and over 9 mm thick black API steel blind casing and one 5.6 m long 12 inch ND screen with slot size of 4 mm. The lower part is cased to 502 m depth with 6 5/8 inch ND Johnson stainless steel casing and screen imported by the Client for this purpose. The casing arrangement is given below:

Table 2 Casing arrangement HBKW4

| type | material | Diameter | count | size | length | top | bottom |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Bottom pipe | 304 | 6 5/8 | 1 | 1 | 1 | 501 | 502 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 495.29 | 501 |
| Casing | 304 | 6 5/8 | 3 | 5.66 | 16.98 | 478.31 | 495.29 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 472.6 | 478.31 |
| Casing | 304 | 6 5/8 | 4 | 5.66 | 22.64 | 449.96 | 472.6 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 444.25 | 449.96 |
| Casing | 304 | 6 5/8 | 7 | 5.66 | 39.62 | 404.63 | 444.25 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 398.92 | 404.63 |
| Casing | 304 | 6 5/8 | 1 | 5.66 | 5.66 | 393.26 | 398.92 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 387.55 | 393.26 |
| Casing | 304 | 6 5/8 | 5 | 5.66 | 28.3 | 359.25 | 387.55 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 353.54 | 359.25 |
| Casing | 304 | 6 5/8 | 1 | 5.66 | 5.66 | 347.88 | 353.54 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 342.17 | 347.88 |
| Casing | 304 | 6 5/8 | 3 | 5.66 | 16.98 | 325.19 | 342.17 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 319.48 | 325.19 |
| Casing | 304 | 6 5/8 | 3 | 5.66 | 16.98 | 302.5 | 319.48 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 296.79 | 302.5 |
| Casing | 304 | 6 5/8 | 5 | 5.66 | 28.3 | 268.49 | 296.79 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 262.78 | 268.49 |
| Casing | 304 | 6 5/8 | 7 | 5.66 | 39.62 | 223.16 | 262.78 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 217.45 | 223.16 |
| Casing | 304 | 6 5/8 | 3 | 5.66 | 16.98 | 200.47 | 217.45 |
| Screen | 304 | 6 5/8 | 1 | 5.71 | 5.71 | 194.76 | 200.47 |
| Casing | 304 | 6 5/8 | 8 | 5.66 | 45.28 | 149.48 | 194.76 |
| Reducer | API/304 | 6-12 | 1 | 1 | 1 | 148.48 | 149.48 |
| Screen | API | 12 | 1 | 5.8 | 5.8 | 142.68 | 148.48 |
| Casing | API | 12 | 25 | 5.8 | 145 | -2.32 | 142.68 |

The 6 5/8 inch casings and screens were fixed in the centre of the borehole using stainless steel centralizers every 12 meter. The annular space between the casing and the borehole wall is filled with washed, rounded basalt river gravel of 9 to 12 mm diameter. The filling of the gravel continued during the well development and end of the pumping test. A total of 14 m3 of gravel is packed to 22 m depth of the well.

Figure 2 Washed basalt gravel

## Development

After the installation of casing, screen and gravel, the mud was thinned and a solution of 17 kg/m3 polyphosphate and 2.25 kg/m3 hypochlorite was injected into the well at every screened section to break the mud cake on the borehole wall. After surging and agitation the solution was left in the well for 24 hours.

Development by airlifting was carried out using a 25 bar compressor and 3 inch airline. Both airlifting and surging techniques were used to clean the well and remove the mud from the surrounding aquifer.

Figure 3 Development by airlifting

# Pumping tests

A submersible pump with a power of 120 kW was set at 140m depth, connected with 8 inch galvanized steel  riser pipes to carry out the pumping tests. Power was supplied by a 200 kW generator with diesel engine. Four tests were carried out: one provisional pumping test for two hours with 45 lps, a 8 hour well performance test (step test with four steps), a 5 day constant discharge test at 30 lps (aquifer test) followed by a recovery test.

The purpose of the step test was to assess the efficiency of the well at different discharges and to determine the safe yield of the well and best pump capacity and setting. The aquifer test was carried out to determine the aquifer properties and ascertain the sustainability of the production.

## Step test

The performance of the well was tested by four steps of two hours each with increasing discharge. The complete data are attached as annexe 2. The table below presents a summary of the test.

Table 3 Step drawdown test

| step | discharge |  | water level | drawdown | specific drawdown | efficiency |
| --- | --- | --- | --- | --- | --- | --- |
|  | m3/h | lps | m | m | m/m3/h | % |
| 1 | 72 | 20 | 72.2 | 20.74 | 0.288 | 94% |
| 2 | 90 | 25 | 90.85 | 39.39 | 0.438 | 93% |
| 3 | 104 | 29 | 96.92 | 45.46 | 0.435 | 92% |
| 4 | 122 | 34 | 106.31 | 54.85 | 0.448 | 91% |

Figure 4 Discharge - drawdown graph of step test

The well efficiency is calculated using Cooper-Jacob’s method:

ε= BQs

and

s=BQ+CQ2

where

ε = efficiency (%)

s = drawdown (m)

Q = discharge (m3/h)

B = linear well loss coefficient (1.4569)

C = non-linear well loss coefficient (0.004384)

The efficiency was calculated to be more than 90%. This means that the head losses due to the well construction are low.

## Aquifer test

A pumping test with constant discharge (30 lps or 108 m3/h) was executed for a period of 5 days. At the end of the test the drawdown was 54.94 meter (water level: 102.32 m bgl), the electrical conductivity was 789 µS/cm and the temperature 35.1 °C. The complete dataset is attached as Annex 3 while the drawdown graph is presented below:

Figure 5 Time - drawdown graph of aquifer test (30 lps)

Three distinctive period can be distinguished on the drawdown curve. The first part of the curve shows fluctuations due to the effect of casing storage and variations in discharge.  After 10 minutes the casing storage effect is negligible and the slope of the drawdown curve is governed by aquifer properties near the well. After 2000 minutes a small increase in the slope is noticed. This slope is used to determine the regional transmissivity 63 m2/d and the long term sustainability.

During the aquifer test the drawdown in HBKW3 was recorded using an automatic data logger. The drawdown graph of HBKW3 is shown on figure 7 below:

Figure 6 Drawdown in HBKW3 during aquifer test on HBKW4

After 7200 minutes of continuous  pumping with 30 lps from HBKW4, the water level has dropped 4 meter in HBKW3. The distance between HBKW3 and HBKW4 is 326 meter. Jacob’s approximation of Theis’s method has been applied to obtain a value for the storativity :

S= 2.25 T t0r2

Where:

S = storativity (5.12 e-4)

T = transmissivity (194 m2/d)

t0  = maximum time with s = 0 (0.125 d)

r = distance to observation well (326 m)

The transmissivity calculated from the drawdown in HBKW3 is considerably larger as compared to HBKW4 , suggesting heterogeneous aquifer properties. The storativity was calculated as 5.12e-4, indicating confined conditions.

## Recovery test

After the aquifer test the recovery of the water level was recorded for 1440 minutes (24 hours). The recovery graph is shown on figure 8. Figure 9 shows the corrected graph that is used to estimate the transmissivity according to Theis’ recovery method (152 m2/d).

Figure 7 Recovery test on HBKW4

Figure 8 Theis’ recovery graph for HBKW4

# Water quality

Three water samples were taken during the pumping test and have been analysed at Water Works Design and Supervision Enterprise lab in Addis Ababa on 13 May 2016.

The water has a temperature of 35.1 °C and is of bicarbonate type with an EC of 659 µS/cm, TDS of 396 mg/l and a total hardness of 30 mg/l CaCO3. The fluoride content of 1.44 mg/l is close to the WHO limit for drinking water.

Full analysis of the three samples is attached as Annexe 4

# Recommended operation

The maximum depth of the pump is the top of the first screen (142.5 m) . The required net positive suction head for a typical submersible pump (NPSH) is around 5.5 meter. Therefore,  water level should not drop below 137 meter.

The surrounding wells (HBKW1,2 and 3) will cause interference and an regional drop of water levels is to be expected (caused by increasing abstractions from the aquifer by AWSSA). Ten meter interference from nearby wells and 10 meter regional drop is adopted as safety margin for the next 10 years. This limits the maximum dynamic water level to 117 meter bgl.

The development of water levels in the  next 10 years has been estimated using Theis’ formula and the aquifer properties calculated from the pumping tests. Figure 10 shows the development of the water levels in HBKW4 for three different scenarios: 90, 110 and 130 m3/h, assuming 85% operation. With the 130 m3/h scenario the water level drops below the safety limit of 117 meter after one year of operation. A design capacity of 110 m3/h (30.5 lps) maximizes the production and keeps the drawdown within set limits. With 85% operation the yearly production would be 825,000 m3 (7500 running hours).

Figure 9 Development of dynamic water level in HBKW4 due to pumping at 90, 110 and 130 m3/h

Annex 1 – Well log

Annex 2 - Step test

Annex 3 – Aquifer test

| Time (min); Water Level (m bgl); Drawdown (m); Discharge (l/s); EC (µS/cm); Temp (°C). 0; 47.38. 1; 75.6; 28.22; 35; 456; 26.8. 2; 78.95; 31.57; 34; 510; 28.2. 3; 81.46; 34.08; 33.5; 461; 29.5. 4; 85.27; 37.89; 33; 692; 29.6. 5; 87.91; 40.53; 33; 752; 30.4. 6; 88.56; 41.18; 31; 766; 31.1. 7; 89.13; 41.75; 31; 769; 28.5. 8; 89.52; 42.14; 30; 760; 28.4. 9; 89.72; 42.34; 30; 775; 29.5. 10; 89.9; 42.52; 30; 787; 26.5. 12; 90.14; 42.76; 30; 790; 27.8. 14; 90.17; 42.79; 30; 787; 29.6. 16; 90.21; 42.83; 30; 776; 29.5. 18; 90.24; 42.86; 30; 746; 30.1. 20; 90.28; 42.9; 30; 791; 33.5. 25; 90.37; 42.99; 30; 785; 34.8. 30; 90.79; 43.41; 30; 760; 33.9. 35; 90.97; 43.59; 30; 807; 33.5. 40; 91.1; 43.72; 30; 810; 33.5. 45; 91.34; 43.96; 30; 809; 33.5. 50; 91.72; 44.34; 30; 830; 32.6. 60; 92.6; 45.22; 30; 860; 32.4. 70; 93.02; 45.64; 30; 840; 32.6. 80; 93.3; 45.92; 30; 820; 31.9. 90; 93.52; 46.14; 30; 825; 32.1. 100; 93.6; 46.22; 30; 842; 32.5. 120; 93.76; 46.38; 30; 846; 32.7. 140; 94.11; 46.73; 30; 855; 32.4. 160; 94.36; 46.98; 30; 860; 32.5. 180; 94.63; 47.25; 30; 872; 33.1. 210; 94.71; 47.33; 30; 876; 35.4. 240; 94.77; 47.39; 30; 877; 35. 270; 94.93; 47.55; 30; 871; 34.8. 300; 95.12; 47.74; 30; 868; 33.5. 330; 95.2; 47.82; 30; 867; 33.4. 360; 95.26; 47.88; 30; 869; 33.6. 420; 95.44; 48.06; 30; 871; 33.3. 480; 95.64; 48.26; 30; 879; 32.9. 540; 95.87; 48.49; 30; 872; 33.2. 600; 96.15; 48.77; 30; 870; 33.3. 660; 96.4; 49.02; 30; 871; 33.2. 720; 96.57; 49.19; 30; 860; 34.9. 780; 96.83; 49.45; 30; 856; 35.3. 840; 96.9; 49.52; 30; 849; 35.5. 900; 97.07; 49.69; 30; 825; 35.8. 960; 97.23; 49.85; 30; 813; 38.9. 1020; 97.34; 49.96; 30; 808; 36. 1080; 97.45; 50.07; 30; 794; 36.1. 1140; 97.58; 50.2; 30; 782; 36.2. 1200; 97.66; 50.28; 30; 780; 36.4. 1260; 97.72; 50.34; 30; 781; 36.1. 1320; 97.77; 50.39; 30; 781; 36.2. 1380; 97.84; 50.46; 30; 782; 36.2. 1440; 98.05; 50.67; 30; 784; 35.8. 1500; 98.08; 50.7; 30; 788; 35.4. 1560; 98.1; 50.72; 30; 766; 36.1. 1620; 98.1; 50.72; 30; 786; 35.4. 1680; 98.1; 50.72; 30; 784; 35.7. 1740; 98.12; 50.74; 30; 788; 35.6. 1800; 98.3; 50.92; 30; 786; 35.3. 1860; 98.31; 50.93; 30; 780; 35.9. 1920; 98.33; 50.95; 30; 785; 35.6. 1980; 98.59; 51.21; 30; 789; 35.4. 2040; 98.77; 51.39; 30; 786; 35.5. 2100; 98.92; 51.54; 30; 784; 35.7. 2160; 98.94; 51.56; 30; 780; 35.9. 2220; 98.96; 51.58; 30; 778; 36.1. 2280; 99.07; 51.69; 30; 779; 36.1. 2340; 99.17; 51.79; 30; 781; 36.1. 2400; 99.3; 51.92; 30; 776; 36.2. 2460; 99.38; 52; 30; 777; 36.2. 2520; 99.45; 52.07; 30; 779; 36.1. 2580; 99.53; 52.15; 30; 774; 36.1. 2640; 99.61; 52.23; 30; 770; 35.9. 2700; 99.72; 52.34; 30; 773; 35.7. 2760; 99.72; 52.34; 30; 804; 33.5. 2820; 99.72; 52.34; 30; 805; 33.7. 2880; 99.74; 52.36; 30; 810; 34.2. 2940; 99.83; 52.45; 30; 814; 33.5. 3000; 100.6; 53.22; 30; 818; 34.6. 3060; 100.71; 53.33; 30; 809; 34.5. 3120; 100.71; 53.33; 30; 809; 34.7. 3180; 100.71; 53.33; 30; 808; 34.9. 3240; 100.71; 53.33; 30; 804; 34.8. 3300; 100.75; 53.37; 30; 810; 34.8. 3360; 100.75; 53.37; 30; 814; 35. 3420; 100.93; 53.55; 30; 816; 34.8. 3480; 100.96; 53.58; 30; 810; 34.9. 3540; 101.02; 53.64; 30; 802; 35.1. 3600; 101.06; 53.68; 30; 794; 35.2. 3660; 101.08; 53.7; 30; 792; 35.2. 3720; 101.19; 53.81; 30; 789; 35.3. 3780; 101.28; 53.9; 30; 790; 35.4. 3840; 101.38; 54; 30; 791; 35.5. 3900; 101.5; 54.12; 30; 788; 35.5. 3960; 101.54; 54.16; 30; 786; 35.4. 4020; 101.61; 54.23; 30; 784; 35.4. 4080; 101.62; 54.24; 30; 785; 35.3. 4140; 101.64; 54.26; 30; 789; 35.1. 4200; 101.66; 54.28; 30; 790; 34.9. 4260; 101.81; 54.43; 30; 804; 34.3. 4320; 101.81; 54.43; 30; 810; 34.8. 4380; 101.81; 54.43; 30; 814; 35.5. 4440; 101.65; 54.27; 30; 816; 36. 4500; 101.35; 53.97; 30; 789; 35.6. 4560; 101.4; 54.02; 30; 790; 36.1. 4620; 101.46; 54.08; 30; 788; 35.3. 4680; 101.78; 54.4; 30; 792; 36.4. 4740; 101.92; 54.54; 30; 796; 36. 4800; 102.02; 54.64; 30; 786; 24.9. 4860; 102.07; 54.69; 30; 794; 34.8. 4920; 102.08; 54.7; 30; 781; 35.3. 4980; 102.09; 54.71; 30; 779; 35.4. 5040; 102.1; 54.72; 30; 778; 35.6. 5100; 102.13; 54.75; 30; 777; 35.7. 5160; 102.25; 54.87; 30; 779; 35.8. 5220; 102.33; 54.95; 30; 781; 36. 5280; 102.4; 55.02; 30; 780; 36.1. 5340; 102.45; 55.07; 30; 779; 36.2. 5400; 102.46; 55.08; 30; 778; 36. 5460; 102.47; 55.09; 30; 782; 35.9. 5520; 102.49; 55.11; 30; 785; 35.8. 5580; 102.6; 55.22; 30; 783; 35.4. 5640; 102.65; 55.27; 30; 789; 34.5. 5700; 102.7; 55.32; 30; 792; 35.2. 5760; 102.65; 55.27; 30; 810; 34.2. 5820; 102.45; 55.07; 30; 814; 35.3. 5880; 102.3; 54.92; 30; 809; 35.8. 5940; 102.2; 54.82; 30; 805; 36. 6000; 102.1; 54.72; 30; 803; 35.9. 6060; 102.03; 54.65; 30; 801; 35.9. 6120; 101.95; 54.57; 30; 798; 35.8. 6180; 102.03; 54.65; 30; 797; 35.9. 6240; 102.18; 54.8; 30; 799; 35.6. 6300; 102.25; 54.87; 30; 802; 34.8. 6360; 102.27; 54.89; 30; 810; 34.1. 6420; 102.33; 54.95; 30; 807; 34.2. 6480; 102.45; 55.07; 30; 805; 34.4. 6540; 102.53; 55.15; 30; 799; 34.7. 6600; 102.65; 55.27; 30; 797; 35.1. 6660; 102.8; 55.42; 30; 801; 35.2. 6720; 102.9; 55.52; 30; 796; 35.3. 6780; 102.95; 55.57; 30; 795; 35.5. 6840; 103; 55.62; 30; 792; 35.7. 6900; 102.9; 55.52; 30; 794; 35.9. 6960; 102.85; 55.47; 30; 789; 36.1. 7020; 102.6; 55.22; 30; 788; 35.9. 7080; 102.56; 55.18; 30; 785; 34.8. 7140; 102.5; 55.12; 30; 784; 34.9. 7200; 102.32; 54.94; 30; 789; 35.1. |  |  |
| --- | --- | --- |

Annex 4 – Water quality